## Signal liste
Signal list for PV Power Plants - TR 3.2.2
Revision: |  | 1.0 | date: | 19.01.2015 |  |  | Specifications for sunspec profiles are available for download at: www.sunspec.org/download. The specifications can be downloaded free of charge by entering name and affiliation. The documentation can subsequently be seen in the zip file at the follwing website address: \Protocol-Information-Conformance-Statements.zip\Protocol Information Conformance Statements\
Category | [13 empty] | Sunspec ID
A | B | C | D | Signal description | Comments | Possible interval | Typical value | Unit | Data types | Purpose of signal | Responsible for signal availability in PCOM | Ancillary services | Energinet.dk reference | Model Prefix Abbrevations | Start Offset | Label
| X | X | X | Swich gear status in POC |  | Open/closed | - | - | Status | Monitor coupling state for netPOC | Meter operator |  | TR 5.8.1 | IC123 | 5 | Conn
| X | X | X | Active power kW - metered in POC | Measurement of active power | 0 - Pmax | - | kW | Metering | Input for settlement | Meter operator |  | TR 5.8.1 | M203 | 19 | Watts
|  | X | X | Active power control - ramp rate constraint | Active power control | Active/inactive | - | - | Control | Activate/deactivate the function | Plant owner | Mandatory ancillary services | TR 5.9.1 | Always active
|  | X | X | Active power control - ramp rate for upward regulation of active power | Active power control | 10 - 300 kW/WTGS/s | 50 kW/WTGS/s | kW/second | Set point | Speed control for upward regulation of active power | Plant owner | Mandatory ancillary services | TR 5.9.1 | IC123 | 9 | WMaxLimPct_RmpTms
|  | X | X | Active power control - ramp rate for downward regulation of active power | Active power control | 10 - 300 kW/WTGS/s | 50 kW/WTGS/s | kW/second | Set point | Control the speed for downward regulation of active power | Plant owner | Mandatory ancillary services | TR 5.9.1 | IC123 | 9 | WMaxLimPct_RmpTms
|  | X | X | Active power control - absolut power constraint | Active power control | Active/inactive | - | - | Control | Activate/deactivate the function | Plant owner | Mandatory ancillary services | TR 5.9.1 | Always active
|  | X | X | Active power control - desired maximum active power | Active power control | 0 - Pmax | - | kW | Set point | Input for controlling active power supplied from a PV power plant | Plant owner | Mandatory ancillary services | TR 5.9.1 | IC123 | 6 | WMaxLimPct
|  | X | X | Active power control - delta constraint | Active power control | Active/inactive | - |  | Control | Activate/deactivate the function | Plant owner | Optional ancillary services | TR 5.8.1 + tender documents | N.A.
|  | X | X | Active power control - desired regulating reserve - Pdelta | Frequency control | 0 - Pmax | - | kW | Set point | Input for creating reserves of active power in a PV power plant | Plant owner | Optional ancillary services | TR 5.8.1 + tender documents | N.A.
| X | X | X | Reactiv power Mvar - measured in POC | Reactive power control | Qmin to Qmax | - | kvar. | Metering | Input for reactive power control | Meter operator |  | TR 5.8.1 | M203 | 29 | VAR
|  | X | X | Power factor - measured in POC | Reactive power control | 0 - 1 | - | - | Metering | Input for reactive power control | Plant owner | Mandatory ancillary services | TR 5.9.1 | M203 | 34 | PF
|  | X | X | Power factor - desired PF in POC | Reactive power control | 0 - 1 | 1 | - | Set point | Set point for desired power factor | Plant owner | Mandatory ancillary services | TR 5.9.1 | IC123 | 11 | OutPFSet
|  | X | X | Reactive power control - activated/deactivated | Reactive power control | Active/inactive | - | - | Control | Activate/deactivate the function | Plant owner | Mandatory ancillary services | TR 5.9.1 | IC123 | 23 | VArPct_Ena
|  | X | X | Reactive power control - desired reactive power in POC | Reactive power control | Qmin to Qmax | 0 | kvar. | Set point | Set point for desired Mvar | Plant owner | Mandatory ancillary services | TR 5.9.1 | IC123 | 17 | VArMaxPct
|  | X | X | Voltage - voltage measured in the voltage reference point | Voltage control | Vrefmin - Vrefmax | - | V | Metering | Input for voltage control in POC | Meter operator | Optional ancillary services | TR 5.8.1 + tender documents | M203 | 12 | Voltage LL
|  | X | X | Voltage control - activated/deactivated | Voltage control | Active/inactive | - | - | Control | Activate/deactivate the function | Plant owner | Optional ancillary services | TR 3.2.2 + tender documents | IC126 | 4 | ModEna
|  | X | X | Voltage control - voltage measured in POC | Voltage control | Umin to Umax | - | V | Metering | Monitor voltage condition in a PV power plant | Plant owner | Optional ancillary services | TR 3.2.2 + tender documents | M203 | 12 | Voltage LL
|  | X | X | Voltage control - voltage control droop | Voltage control | 2 - 6% | 4% | % of Un | Set point | Droops for voltage stabilisation in POC | Plant owner | Optional ancillary services | TR 3.2.2 + tender documents | N.A.
|  | X | X | Voltage control - desired voltage in voltage reference point | Voltage control | Uref ± 10% | - | V | Set point | Input for voltage stabilisation in POC | Plant owner | Optional ancillary services | TR 3.2.2 + tender documents | N.A.
|  | X | X | Frequency response - activated/deactivated | Frequency response | Active/inactive | - | Hz | Set point | Activate/deactivate the function | Plant owner | Optional ancillary services | TR 5.8.1 + tender documents | IC134 | 4 | ModEna
|  | X | X | Frequency response -initial frequency for frequency response - fR | Frequency response | 50.00 - 50.50 | 50.20 | Hz | Set point | Input for frequency stabilisation | Plant owner | Optional ancillary services | TR 5.8.1 + tender documents | IC134 | 14-53 | Hz, W
|  | X | X | Frequency control - frequency measured in POC | Frequency control | 47.00 - 52.00 | - | - | Status | Input for frequency stabilisation in POC | Meter operator |  | TR 5.8.1 | M203 | 17 | Hz, W
|  | X | X | Frequency control - activated/deactivated | Frequency control | Active/inactive | - | - | Status | Activate/deactivate the function | Plant owner | Mandatory ancillary services | TR 5.9.1 | N.A.
|  | X | X | Reference frequency - desired frequency in POC - fref | Frequency control | 50.00 | 50.00 | Hz | Set point | Input for frequency stabilisation in POC | Plant owner | Mandatory ancillary services | TR 5.9.1 | N.A.
|  | X | X | Frequency control - control limit - low - fmin | Frequency control | 46.50 - 47.50 | 47.00 | Hz | Set point | Lower control limit value for frequency control | Plant owner | Mandatory ancillary services | TR 5.9.1 | N.A.
|  | X | X | Frequency control - control limit - high - fmax | Frequency control | 51.00 - 52.50 | 52.00 | Hz | Set point | Upper control limit value for frequency control | Plant owner | Mandatory ancillary services | TR 5.9.1 | N.A.
|  | X | X | Frequency control - initial frequency for control band and frequency respons- f1 | Frequency control | 49.50 - 50.00 | 49.80 or 50.20 | Hz | Set point | Input for frequency stabilisation in POC | Plant owner | Optional ancillary services | TR 5.8.1 + tender documents | N.A.
|  | X | X | Frequency control - initial frequency for dead band - f2 | Frequency control | 49.80 - 50.00 | 49.88 | Hz | Set point | Input for frequency stabilisation in POC | Plant owner | Optional ancillary services | TR 5.8.1 + tender documents | N.A.
|  | X | X | Frequency control - final frequency for dead band - f3 | Frequency control | 50.00 - 50.20 | 50.02 | Hz | Set point | Input for frequency stabilisation in POC | Plant owner | Optional ancillary services | TR 5.8.1 + tender documents | N.A.
|  | X | X | Frequency control - final frequency for control band - f4 | Frequency control | 50.00 - 50.50 | 50.20 | Hz | Set point | Input for frequency stabilisation in POC | Plant owner | Optional ancillary services | TR 5.8.1 + tender documents | N.A.
|  | X | X | Frequency control - final frequency for regulation up to f5 | Frequency control | 51.00 - 52.00 | 51.25 | Hz | Set point | Input for frequency stabilisation in POC | Plant owner | Mandatory ancillary services | TR 5.9.1 | N.A.
|  | X | X | Frequency control - final frequency for control up to f6 | Frequency control | 51.00 - 52.00 | 51.75 | Hz | Set point | Input for frequency stabilisation in POC | Plant owner | Mandatory ancillary services | TR 5.9.1 | N.A.
|  | X | X | Frequency control - droop 1 for control from f1 to f2 | Frequency control | 2 -8% | 4% | % of Pn | Set point | Input for frequency stabilisation in POC | Plant owner | Optional ancillary services | TR5 .8.1 + tender documents | N.A.
|  | X | X | Frequency control - droop 2 for control from f3 to f4 | Frequency control | 2 - 8% | 6% | % of Pn | Set point | Input for frequency stabilisation in POC | Plant owner | Optional ancillary services | TR 5.8.1 + tender documents | N.A.
|  | X | X | Frequency control - droop 3 for control from f4 to f5 | Frequency control | 2 - 10% | 8% | % af Pn | Set point | Input for frequency stabilisation in POC | Plant owner | Mandatory ancillary services | TR 5.9.1 | N.A.
|  | X | X | Frequency control - droop 4 for downward regulation from f5 to f6 | Frequency control | 5 - 20% | 10% | % of Pn | Set point | Input for frequency stabilisation in POC | Plant owner | Mandatory ancillary services | TR 5.9.1 | N.A.
|  | X | X | Frequency control - frequency limit for reclosure, if active power has been reduced to below Pmin - f7 | Frequency control | 50.00 - 50.10 | 50.05 | Hz | Set point | Input for frequency stabilisation in POC | Plant owner | Mandatory ancillary services | TR 5.9.1 | N.A.
|  | X | X | System protection | System protection | Active/inactive | - | - | Control | Activate/deactivate the function | Plant owner | Mandatory ancillary services | TR 5.9.1 | IC123 | 6 | WMaxLimPct
X | X | X | X | Stop signal | System protection | Active/inactive | - | - | Control | Activation/deactivation of the plant | Plant owner | Mandatory ancillary services | TR 5.9.1 | IC123 | 5 | Conn = 0
X | X | X | X | On-hold signal - "Released for start" | System protection | Active/inactive | - | - | Control | Activation/deactivation of start of the plant | Plant owner | Mandatory ancillary services | TR 5.9.1 | IC123 | 5 | Conn = 1
Note on P7: Søren Bækhøj Kjær: Den brugte parameter fra sunspec giver tilstanden for bryderen i én inverter. Hvis man ønkser at overvåge tilstanden for bryderen ved POC, så skal man anvende IEC 61850 standard for substation automation.
Note on P8: Søren Bækhøj Kjær: Man kan også bruge de målte data fra inverteren, såfremt man anvender følgende parameter: I103-15 (Watts).
Note on P11: Søren Bækhøj Kjær: pt. findes der kun én gradient for aktiv effekt.
Note on P14: Søren Bækhøj Kjær: Findes ikke i iec 61850-90-7. Her må energinet.dk tage det op i relevante WG således det kommer med i iec61850-90-7 og derfra kommer med i sunspec profilerne.
Note on P15: Søren Bækhøj Kjær: Findes ikke i iec 61850-90-7. Her må energinet.dk tage det op i relevante WG således det kommer med i iec61850-90-7 og derfra kommer med i sunspec profilerne.
Note on P16: Søren Bækhøj Kjær: Man kan også bruge de målte data fra inverteren, såfremt man anvender følgende parameter: I103-21 (VAr).
Note on P17: Søren Bækhøj Kjær: Man kan også bruge de målte data fra inverteren, såfremt man anvender følgende parameter: I103-23 (PF).
Note on P19: Søren Bækhøj Kjær: Gælder kun for aktivering af Q-regulering, ikke PF.
Note on P21: Søren Bækhøj Kjær: Man kan også bruge de målte data fra inverteren, såfremt man anvender følgende parameter: I103-8,9,10 Phase voltages AB, BC, CA).
Note on P23: Søren Bækhøj Kjær: Man kan også bruge de målte data fra inverteren, såfremt man anvender følgende parameter: I103-8,9,10 Phase voltages AB, BC, CA).
Note on P24: Søren Bækhøj Kjær: iec61850-90-7 opererer ikke med en statik, men med støttepunkter for en look up table. Dette bør inkluderes i TF 3.2.2
Note on P25: Søren Bækhøj Kjær: iec61850-90-7 opererer ikke med en statik, men med støttepunkter for en look up table. Dette bør inkluderes i TF 3.2.2
Note on P27: Søren Bækhøj Kjær: Frekvens respons i iec 61850-90-7 opererer ikke kun med én værdi, men med en hel række værdier i en look up tabel, ligesom for frekvens kontrol. Dette bør der rettes op på i TF 3.2.2.
Note on P28: Søren Bækhøj Kjær: Man kan også bruge de målte data fra inverteren, såfremt man anvender følgende parameter: I103-17 (Hz).
Note on P29: Søren Bækhøj Kjær: Findes ikke i iec 61850-90-7. Her må energinet.dk tage det op i relevante WG således det kommer med i iec61850-90-7 og derfra kommer med i sunspec profilerne. Eventuelt kunne low/high frequency ride through i iedc61850-90-7 tilpasses til formålet.